## Sheet1
All Registers:
Request type: | 16bit Unsigned Integer
Function Code: | 0x03 Holding Registers
PLC ID: | 1
Register Num | Register Name | Controller scales up by: | Editable (From HMI) | Type after scaling | Description
0 | profile1_T0 | E1 | yes | Decimal | First profile, 1st temperature
1 | profile1_T1 | E1 | yes | Decimal | First profile, 2nd temperature
2 | profile1_T2 | E1 | yes | Decimal | First profile, 3rd temperature
3 | profile1_T3 | E1 | yes | Decimal | First profile, 4th temperature
4 | profile1_T4 | E1 | yes | Decimal | First profile, 5th temperature
5 | profile2_T0 | E1 | yes | Decimal | Second profile, 1st temperature
6 | profile2_T1 | E1 | yes | Decimal | Second profile, 2nd temperature
7 | profile2_T2 | E1 | yes | Decimal | Second profile, 3rd temperature
8 | profile2_T3 | E1 | yes | Decimal | Second profile, 4th temperature
9 | profile2_T4 | E1 | yes | Decimal | Second profile, 5th temperature
10 | profile_t0 | E1 | yes | Decimal | Common time step for both profiles
11 | profile_t1 | E1 | yes | Decimal | -
12 | profile_t2 | E1 | yes | Decimal | -
13 | profile_t3 | E1 | yes | Decimal | -
14 | profile_t4 | E1 | yes | Decimal | -
15 | p0 | E2 | yes | Decimal | "P" value for 1st heater PID Loop
16 | i0 | E2 | yes | Decimal | "I" value for 1st heater PID Loop
17 | d0 | E2 | yes | Decimal | "D" value for 1st heater PID Loop
18 | m0 | E3 | yes | Decimal | "M" value for linear scaling of rtd
19 | b0 | E1 | yes | Decimal | "B" value for linear scaling of rtd
20 | rref0 | None | yes | Integer | Reference resistor value in rtd Module
21 | p1 | E2 | yes | Decimal | -
22 | i1 | E2 | yes | Decimal | -
23 | d1 | E2 | yes | Decimal | -
24 | m1 | E3 | yes | Decimal | -
25 | b1 | E1 | yes | Decimal | -
26 | rref1 | None | yes | Integer | -
27 | p2 | E2 | yes | Decimal | -
28 | i2 | E2 | yes | Decimal | -
29 | d2 | E2 | yes | Decimal | -
30 | m2 | E3 | yes | Decimal | -
31 | b2 | E1 | yes | Decimal | -
32 | rref2 | None | yes | Integer | -
33 | p3 | E2 | yes | Decimal | -
34 | i3 | E2 | yes | Decimal | -
35 | d3 | E2 | yes | Decimal | -
36 | m3 | E3 | yes | Decimal | -
37 | b3 | E1 | yes | Decimal | -
38 | rref3 | None | yes | Integer | -
39 | p4 | E2 | yes | Decimal | -
40 | i4 | E2 | yes | Decimal | -
41 | d4 | E2 | yes | Decimal | -
42 | m4 | E3 | yes | Decimal | -
43 | b4 | E1 | yes | Decimal | -
44 | rref4 | None | yes | Integer | -
45 | p5 | E2 | yes | Decimal | -
46 | i5 | E2 | yes | Decimal | -
47 | d5 | E2 | yes | Decimal | -
48 | m5 | E3 | yes | Decimal | -
49 | b5 | E1 | yes | Decimal | -
50 | rref5 | None | yes | Integer | -
51 | p6 | E2 | yes | Decimal | -
52 | i6 | E2 | yes | Decimal | -
53 | d6 | E2 | yes | Decimal | - | 2.39
54 | m6 | E3 | yes | Decimal | -
55 | b6 | E1 | yes | Decimal | -
56 | rref6 | None | yes | Integer | -
57 | setpoint0 | E1 | yes | Decimal | Setpoint for 1st heater
58 | setpoint1 | E1 | yes | Decimal | Setpoint for 2nd heater
59 | setpoint2 | E1 | yes | Decimal | Setpoint for 3rd heater
60 | setpoint3 | E1 | yes | Decimal | Setpoint for 4th heater
61 | setpoint4 | E1 | yes | Decimal | Setpoint for 5th heater
62 | setpoint5 | E1 | yes | Decimal | Setpoint for 6th heater
63 | setpoint6 | E1 | yes | Decimal | Setpoint for 7th heater
64 | setpoint_heat_time | E1 | yes | Decimal | How long (in seconds) setpoint mode runs
65 | cool_time | E1 | yes | Decimal | How long (in seconds) to run the cooling air directly after heating
66 | save_time | E1 | yes | Decimal | How long (in seconds) to save current configuration to memory
67 | max_setpoint | E1 | yes | Decimal | Configures the maximum settable setpoint for all channels
68 | heat | None | yes | Boolean(0/1) | Switches between Heating (1) and Not heating (0)
69 | mode | None | yes | Boolean(0/1) | Switches between Profile Mode (1) and Setpoint Mode (0)
70 | input0 | E1 | no | Decimal | "input" is the measured temperature in °C. Used for displaying the temperature and as feedback for the PID loop
71 | input1 | E1 | no | Decimal | -
72 | input2 | E1 | no | Decimal | -
73 | input3 | E1 | no | Decimal | -
74 | input4 | E1 | no | Decimal | -
75 | input5 | E1 | no | Decimal | -
76 | input6 | E1 | no | Decimal | -
77 | output0 | E1 | no | Decimal | "output" is the amount of power that the controller is driving represented as a percentange. Calculated by PID loop
78 | output1 | E1 | no | Decimal | -
79 | output2 | E1 | no | Decimal | -
80 | output3 | E1 | no | Decimal | -
81 | output4 | E1 | no | Decimal | -
82 | output5 | E1 | no | Decimal | -
83 | output6 | E1 | no | Decimal | -
84 | instruction | None | no | Integer | Unused, existed to change to a different item in a list of instructions in the hmi
85 | error_codes | None | no | binary | Displays which error has occurred represented as a binary number
86 | warning_codes | None | no | binary | Displays which warning has occurred represented as a binary number
87 | start_percent | E0 | yes | Decimal | For temperature dependant output scaling: the max output at room temperature
88 | room_temp | E1 | yes | Decimal | For temperature dependant output scaling: the value of room temperaure set by the user
89 | max_temp | E1 | yes | Decimal | For temperature dependant output scaling: the temperature where output reaches 100%
90 | slope1_T0 | None | yes | Boolean(0/1) | Determines wether the current step will slope linearly to the given temperature for the step
91 | slope1_T1 | None | yes | Boolean(0/1) | -
92 | slope1_T2 | None | yes | Boolean(0/1) | -
93 | slope1_T3 | None | yes | Boolean(0/1) | -
94 | slope1_T4 | None | yes | Boolean(0/1) | -
95 | slope2_T0 | None | yes | Boolean(0/1) | -
96 | slope2_T1 | None | yes | Boolean(0/1) | -
97 | slope2_T2 | None | yes | Boolean(0/1) | -
98 | slope2_T3 | None | yes | Boolean(0/1) | -
99 | slope2_T4 | None | yes | Boolean(0/1) | -
100 | trigger_input | None | no | Boolean(0/1) | monitors pin A0, closes relay R5 both labeled on controller
101 | heater_cooling | None | yes | Boolean(0/1) | turns cooling on and off (automatically toggled in profile mode after heating for durration of "cool_time" or register 65)
102 | gp_relay | None | yes | Boolean(0/1) | closes contact labeled "R8" on controller
103 | thermocouple reading | E1 | no | Decimal
104 | camera_on_temp | E1 | yes | Decimal | the temperature at which the square wave pulse is sent
105 | camera_on_frequency | None | yes | Integer | the frequency of the square wave pulse to send
106 | serial_streaming | None | yes | Boolean(0/1) | 1 enables serial streaming on main port, 0 disables it